## IO
Description | PLC | Signal Type | Object | Address | IO Check | HMI Animation | HMI Alarm | Notes
Pump #1 Overload Fault | LST1_CMPLX | DI | LST1 Pump #1 | Local:1:I.DATA.0 | x | x | x
Pump #1 In Auto | LST1_CMPLX | DI | LST1 Pump #1 | Local:1:I.DATA.1 | x | x | x
Pump #2 Overload Fault | LST1_CMPLX | DI | LST1 Pump #2 | Local:1:I.DATA.2 | x | x | x
Pump #2 In Auto | LST1_CMPLX | DI | LST1 Pump #2 | Local:1:I.DATA.3 | x | x | x
Pump #1 Motor High Temp | LST1_CMPLX | DI | LST1 Pump #2 | Local:1:I.DATA.7 | x | x | x
Pump #2 Motor High Temp | LST1_CMPLX | DI | LST1 Pump #2 | Local:1:I.DATA.9 | x | x | x
Low Level Float Alarm | LST1_CMPLX | DI | LST1 LoLv | Local:1:I.DATA.10 | x | x | x
High Level Float Alarm | LST1_CMPLX | DI | LST1 HiLv | Local:1:I.DATA.11 | x | x | x
Pump #1 Running | LST1_CMPLX | DI | LST1 Pump #1 | Local:1:I.DATA.13 | x | x
Pump #2 Running | LST1_CMPLX | DI | LST1 Pump #2 | Local:1:I.DATA.14 | x | x
Pump #1 Start/Stop | LST1_CMPLX | DO | LST1 Pump #1 | Local:2:O.DATA.0 | x
Pump #2 Start/Stop | LST1_CMPLX | DO | LST1 Pump #2 | Local:2:O.DATA.1 | x
Wetwell Level | LST1_CMPLX | AI | LST1 Lv | Local:3:I.CH0DATA | x | x
Feed Pump #1 In Auto | WWTP_CLX | DI | WWTP Feed Pump #1 | WWTP_CLX_Rack01_Slot00_CNB:I.SLOT[1].DATA.0 | x | x
Feed Pump #1 Running | WWTP_CLX | DI | WWTP Feed Pump #1 | WWTP_CLX_Rack01_Slot00_CNB:I.SLOT[1].DATA.1 | x | x
Feed Pump #1 Fault | WWTP_CLX | DI | WWTP Feed Pump #1 | WWTP_CLX_Rack01_Slot00_CNB:I.SLOT[1].DATA.2 | x | x | x
Feed Pump #1 OverLoad | WWTP_CLX | DI | WWTP Feed Pump #1 | WWTP_CLX_Rack01_Slot00_CNB:I.SLOT[1].DATA.3 | x | x | x
Feed Pump #2 In Auto | WWTP_CLX | DI | WWTP Feed Pump #2 | WWTP_CLX_Rack01_Slot00_CNB:I.SLOT[1].DATA.4 | x | x
Feed Pump #2 Running | WWTP_CLX | DI | WWTP Feed Pump #2 | WWTP_CLX_Rack01_Slot00_CNB:I.SLOT[1].DATA.5 | x | x
Feed Pump #2 Fault | WWTP_CLX | DI | WWTP Feed Pump #2 | WWTP_CLX_Rack01_Slot00_CNB:I.SLOT[1].DATA.6 | x | x | x
Feed Pump #2 OverLoad | WWTP_CLX | DI | WWTP Feed Pump #2 | WWTP_CLX_Rack01_Slot00_CNB:I.SLOT[1].DATA.7 | x | x | x
Feed Pump #2 In Auto | WWTP_CLX | DI | WWTP Feed Pump #2 | WWTP_CLX_Rack01_Slot00_CNB:I.SLOT[1].DATA.8 | x | x
Feed Pump #1 Start/Stop | WWTP_CLX | DO | WWTP Feed Pump #1 | WWTP_CLX_Rack01_Slot00_CNB:O.SLOT[2].DATA.0 | x
Feed Pump #2 Start/Stop | WWTP_CLX | DO | WWTP Feed Pump #2 | WWTP_CLX_Rack01_Slot00_CNB:O.SLOT[2].DATA.1 | x
Alum Tank #1 Level Ind | WWTP_CLX | AI | WWTP Alum Tank Level | WWTP_CLX_Rack01_Slot00_CNB:4:I.CH0DATA | x
Feed Pump #1 Speed Ind | WWTP_CLX | AI | WWTP Feed Pump #1 | WWTP_CLX_Rack01_Slot00_CNB:4:I.CH2DATA | x | x
Feed Pump #2 Speed Ind | WWTP_CLX | AI | WWTP Feed Pump #2 | WWTP_CLX_Rack01_Slot00_CNB:4:I.CH3DATA | x | x
Feed Pump #1 Speed Cmd | WWTP_CLX | AO | WWTP Feed Pump #1 | WWTP_CLX_Rack01_Slot00_CNB:6:O.CH0DATA | x
Feed Pump #2 Speed Cmd | WWTP_CLX | AO | WWTP Feed Pump #2 | WWTP_CLX_Rack01_Slot00_CNB:6:O.CH1DATA | x
Aeration Tank Influent Flow | WWTP_CLX | AI | WWTP Areation Tank influent Flow | ?
Level Switch Low | WWTP_HDWK_CLX | DI | WWTP RW WW Level Switch Low | Local:2:I.DATA.0 | x | x | x | summary ack does not ack plc block
Level Switch High | WWTP_HDWK_CLX | DI | WWTP RW WW Level Switch High | Local:2:I.DATA.1 | x | x | x | summary ack does not ack plc block
Level Switch High-High | WWTP_HDWK_CLX | DI | WWTP RW WW Level Switch High-High | Local:2:I.DATA.2 | x | x | x | summary ack does not ack plc block
Bar Screen #1 In-Auto | WWTP_HDWK_CLX | DI | WWTP Bar Screen #1 | Local:2:I.DATA.3 | x | x
Bar Screen #1 Running | WWTP_HDWK_CLX | DI | WWTP Bar Screen #1 | Local:2:I.DATA.4 | x | x
Bar Screen #2 In-Auto | WWTP_HDWK_CLX | DI | WWTP Bar Screen #2 | Local:2:I.DATA.5 | x | x
Bar Screen #2 Running | WWTP_HDWK_CLX | DI | WWTP Bar Screen #2 | Local:2:I.DATA.6 | x | x
Grit Tank #1 In-Auto | WWTP_HDWK_CLX | DI | WWTP Grit Tank #1 Drive | Local:2:I.DATA.7 | x | x
Grit Tank #1 Running | WWTP_HDWK_CLX | DI | WWTP Grit Tank #1 Drive | Local:2:I.DATA.8 | x | x
Bar Screen #1 Start/Stop | WWTP_HDWK_CLX | DO | WWTP Bar Screen #1 | Local:3:O.DATA.0 | x | x | x | Start & Stop Fail only
Bar Screen #2 Start/Stop | WWTP_HDWK_CLX | DO | WWTP Bar Screen #2 | Local:3:O.DATA.1 | x | x | x | Start & Stop Fail only
Grit Tank #1 Start/Stop | WWTP_HDWK_CLX | DO | WWTP Grit Tank #1 Drive | Local:3:O.DATA.2 | x | x | x | Start & Stop Fail only
Influent Well Level Indication 0 - 40 Ft | WWTP_HDWK_CLX | AI | WWTP RW WW Level | Local:4:I.CH0DATA | x | x | x | Hi & Lo Alarms only
Bar Screen #1 Screen Monitoring 0-24 Ft | WWTP_HDWK_CLX | AI | WWTP Bar Screen #1 | Local:4:I.CH1DATA | x | x | x | Hi Alarm only
Bar Screen #2 Screen Monitoring 0-24 Ft | WWTP_HDWK_CLX | AI | WWTP Bar Screen #2 | Local:4:I.CH2DATA | x | x | x | Hi Alarm only
Grit Tank #1 Flow 0-20 MGD | WWTP_HDWK_CLX | AI | WWTP Grit Tank #1 Flow | Local:4:I.CH3DATA | x | x |  | No Alarms, IF in maintenace mode, totalizer does not totalize
BLR-400 In-Auto | WWTP_SEC_CLX | DI | WWTP Blower 400 (BLR-400) | Local:2:I.DATA.0 | x | x | na
BLR-400 Running | WWTP_SEC_CLX | DI | WWTP Blower 400 (BLR-400) | Local:2:I.DATA.1 | x | x | x
BLR-400 Fault | WWTP_SEC_CLX | DI | WWTP Blower 400 (BLR-400) | Local:2:I.DATA.2 | x | x | x
Secondary Tank #1 Running | WWTP_SEC_CLX | DI | WWTP Secondary Treatment Tank #1 Drive | Local:2:I.DATA.3 | x | x | x
Secondary Tank #1 In-Auto | WWTP_SEC_CLX | DI | WWTP Secondary Treatment Tank #1 Drive | Local:2:I.DATA.4 | x | x | na
Secondary Tank #1 Torque | WWTP_SEC_CLX | DI | WWTP Secondary Treatment Tank #1 Drive | Local:2:I.DATA.5 | x | x | x | Needs to be displayed in HMI
Secondary Tank #2 Running | WWTP_SEC_CLX | DI | WWTP Secondary Treatment Tank #2 Drive | Local:2:I.DATA.6
Secondary Tank #2 In-Auto | WWTP_SEC_CLX | DI | WWTP Secondary Treatment Tank #2 Drive | Local:2:I.DATA.7
Secondary Tank #2 Torque | WWTP_SEC_CLX | DI | WWTP Secondary Treatment Tank #2 Drive | Local:2:I.DATA.8
M-400 Running | WWTP_SEC_CLX | DI | WWTP Aeration Tank #1 Mixer #1 (M-400) | Local:2:I.DATA.9
M-400 Fault | WWTP_SEC_CLX | DI | WWTP Aeration Tank #1 Mixer #1 (M-400) | Local:2:I.DATA.10
M-400 In-Auto | WWTP_SEC_CLX | DI | WWTP Aeration Tank #1 Mixer #1 (M-400) | Local:2:I.DATA.11
M-401 Running | WWTP_SEC_CLX | DI | WWTP Aeration Tank #1 Mixer #2 (M-401) | Local:2:I.DATA.12
M-401 Fault | WWTP_SEC_CLX | DI | WWTP Aeration Tank #1 Mixer #2 (M-401) | Local:2:I.DATA.13
M-401 In-Auto | WWTP_SEC_CLX | DI | WWTP Aeration Tank #1 Mixer #2 (M-401) | Local:2:I.DATA.14
M-402 Running | WWTP_SEC_CLX | DI | WWTP Aeration Tank #2 Mixer #1 (M-402) | Local:3:I.DATA.0
M-402 Fault | WWTP_SEC_CLX | DI | WWTP Aeration Tank #2 Mixer #1 (M-402) | Local:3:I.DATA.1
M-402 In-Auto | WWTP_SEC_CLX | DI | WWTP Aeration Tank #2 Mixer #1 (M-402) | Local:3:I.DATA.2
M-403 Running | WWTP_SEC_CLX | DI | WWTP Aeration Tank #2 Mixer #2 (M-403) | Local:3:I.DATA.3
M-403 Fault | WWTP_SEC_CLX | DI | WWTP Aeration Tank #2 Mixer #2 (M-403) | Local:3:I.DATA.4
M-403 In-Auto | WWTP_SEC_CLX | DI | WWTP Aeration Tank #2 Mixer #2 (M-403) | Local:3:I.DATA.5
Secondary Tank #1 Start/Stop | WWTP_SEC_CLX | DO | WWTP Secondary Treatment Tank #1 Drive | Local:4:O.DATA.0 | x | x
Secondary Tank #2 Start/Stop | WWTP_SEC_CLX | DO | WWTP Secondary Treatment Tank #2 Drive | Local:4:O.DATA.1
BLR-400 Start/Stop | WWTP_SEC_CLX | DO | WWTP Blower 400 (BLR-400) | Local:4:O.DATA.2 | x | x
M-400 Start/Stop | WWTP_SEC_CLX | DO | WWTP Aeration Tank #1 Mixer #1 (M-400) | Local:4:O.DATA.3
M-401 Start/Stop | WWTP_SEC_CLX | DO | WWTP Aeration Tank #1 Mixer #2 (M-401) | Local:4:O.DATA.4
M-402 Start/Stop | WWTP_SEC_CLX | DO | WWTP Aeration Tank #2 Mixer #1 (M-402) | Local:4:O.DATA.5
M-403 Start/Stop | WWTP_SEC_CLX | DO | WWTP Aeration Tank #2 Mixer #2 (M-403) | Local:4:O.DATA.6
Secondary Tank #1 RAS Control (FIT-400) 0 - 3 MGD | WWTP_SEC_CLX | AI | WWTP Secondary Treatment Tank #1 RAS Pump Discharge Flow (FE-400) | Local:5:I.CH0DATA | x | x |  | missing comm failure (channel fault alarm)
Secondary Tank #2 RAS Control (FIT-401) 0 - 3 MGD | WWTP_SEC_CLX | AI | WWTP Secondary Treatment Tank #2 RAS Pump Discharge Flow (FE-401) | Local:5:I.CH1DATA
PV-600 In-Auto | WWTP_SOLIDS_CLX | DI | WWTP Thickened WAS Tank Influent Position Valve (PV-600) | Local:3:I.DATA.0
P-600 In-Auto | WWTP_SOLIDS_CLX | DI | WWTP Thickened WAS Tank To Solids Tank Pump (P-600) | Local:3:I.DATA.1
P-600 Running | WWTP_SOLIDS_CLX | DI | WWTP Thickened WAS Tank To Solids Tank Pump (P-600) | Local:3:I.DATA.2
P-600 Fault | WWTP_SOLIDS_CLX | DI | WWTP Thickened WAS Tank To Solids Tank Pump (P-600) | Local:3:I.DATA.3
P-601 In-Auto | WWTP_SOLIDS_CLX | DI | WWTP Primary Treatment To Solids Tank Pump (P-601) | Local:3:I.DATA.4
P-601 Running | WWTP_SOLIDS_CLX | DI | WWTP Primary Treatment To Solids Tank Pump (P-601) | Local:3:I.DATA.5
P-601 Fault | WWTP_SOLIDS_CLX | DI | WWTP Primary Treatment To Solids Tank Pump (P-601) | Local:3:I.DATA.6
P-602 In-Auto | WWTP_SOLIDS_CLX | DI | WWTP Solids Tank to Filter Press Pump (P-602) | Local:3:I.DATA.7 | x | x
P-602 Running | WWTP_SOLIDS_CLX | DI | WWTP Solids Tank to Filter Press Pump (P-602) | Local:3:I.DATA.8 | x | x | x
P-602 Fault | WWTP_SOLIDS_CLX | DI | WWTP Solids Tank to Filter Press Pump (P-602) | Local:3:I.DATA.9 | x | x | missing in alarm display
Solids Storage Tank Drive In-Auto | WWTP_SOLIDS_CLX | DI | WWTP Solids Storage Tank #1 Drive | Local:3:I.DATA.10 | x | x
Solids Storage Tank Drive Running | WWTP_SOLIDS_CLX | DI | WWTP Solids Storage Tank #1 Drive | Local:3:I.DATA.11 | x | x | x
Solids Storage Tank Drive Torque | WWTP_SOLIDS_CLX | DI | WWTP Solids Storage Tank #1 Drive | Local:3:I.DATA.12 | x | x | missing in alarm display
Solids Storage Tank Drive #1 Start/Stop | WWTP_SOLIDS_CLX | DO | WWTP Solids Storage Tank #1 Drive | Local:4:O.DATA.0
P-600 Start/Stop | WWTP_SOLIDS_CLX | DO | WWTP Thickened WAS Tank To Solids Tank Pump (P-600) | Local:4:O.DATA.1
P-601 Start/Stop | WWTP_SOLIDS_CLX | DO | WWTP Primary Treatment To Solids Tank Pump (P-601) | Local:4:O.DATA.2
P-602 Start/Stop | WWTP_SOLIDS_CLX | DO | WWTP Solids Tank to Filter Press Pump (P-602) | Local:4:O.DATA.3 | x
From Secondary RAS To GBT Flow (FIT-600) 0-500 GPM | WWTP_SOLIDS_CLX | AI | WWTP Secondary RAS To GBT Flow (FIT-600) 0-500 GPM | Local:5:I.CH0DATA
WAS Storage Tank Level Indication (LIT-603) 0-20 Ft | WWTP_SOLIDS_CLX | AI | WWTP Solids Storage Tank Level Indication (LIT-603) 0-20 Ft | Local:5:I.CH1DATA | x | x | x | io fault missing
WAS Holding Tank Level Indication (LIT-608) 0-20 Ft | WWTP_SOLIDS_CLX | AI | WWTP WAS Storage Tank Level Indication (LIT-605) 0-20 Ft | Local:5:I.CH2DATA | x | x | x | io fault missing, tank not animated
Level Switch Low | WTP_RW_CLX | DI | WTP RW WW Level Switch Low | Local:2:I.DATA.0 | x | x | x | summary ack does not ack plc block
Level Switch High | WTP_RW_CLX | DI | WTP RW WW Level Switch High | Local:2:I.DATA.1 | x | x | x | summary ack does not ack plc block
Level Switch High-High | WTP_RW_CLX | DI | WTP RW WW Level Switch High-High | Local:2:I.DATA.2 | x | x | x | summary ack does not ack plc block
Bar Screen #1 In-Auto | WTP_RW_CLX | DI | WTP Bar Screen #1 | Local:2:I.DATA.3 | x | x
Bar Screen #1 Running | WTP_RW_CLX | DI | WTP Bar Screen #1 | Local:2:I.DATA.4 | x | x
Bar Screen #2 In-Auto | WTP_RW_CLX | DI | WTP Bar Screen #2 | Local:2:I.DATA.5 | x | x
Bar Screen #2 Running | WTP_RW_CLX | DI | WTP Bar Screen #2 | Local:2:I.DATA.6 | x | x
Grit Tank #1 In-Auto | WTP_RW_CLX | DI | WTP Grit Tank #1 Drive | Local:2:I.DATA.7 | x | x
Grit Tank #1 Running | WTP_RW_CLX | DI | WTP Grit Tank #1 Drive | Local:2:I.DATA.8 | x | x
Bar Screen #1 Start/Stop | WTP_RW_CLX | DO | WTP Bar Screen #1 | Local:3:O.DATA.0 | x | x | x | Start & Stop Fail only
Bar Screen #2 Start/Stop | WTP_RW_CLX | DO | WTP Bar Screen #2 | Local:3:O.DATA.1 | x | x | x | Start & Stop Fail only
Grit Tank #1 Start/Stop | WTP_RW_CLX | DO | WTP Grit Tank #1 Drive | Local:3:O.DATA.2 | x | x | x | Start & Stop Fail only
Influent Well Level Indication 0 - 40 Ft | WTP_RW_CLX | AI | WTP RW WW Level | Local:4:I.CH0DATA | x | x | x | Hi & Lo Alarms only
Bar Screen #1 Screen Monitoring 0-24 Ft | WTP_RW_CLX | AI | WTP Bar Screen #1 | Local:4:I.CH1DATA | x | x | x | Hi Alarm only
Bar Screen #2 Screen Monitoring 0-24 Ft | WTP_RW_CLX | AI | WTP Bar Screen #2 | Local:4:I.CH2DATA | x | x | x | Hi Alarm only
Grit Tank #1 Flow 0-20 MGD | WTP_RW_CLX | AI | WTP Grit Tank #1 Flow | Local:4:I.CH3DATA | x | x |  | No Alarms, IF in maintenace mode, totalizer does not totalize
Rapid Mix Basin Drive In-Auto | WTP_SEP_CLX | DI | Rapid Mix Basin Drive | Local:2:I.DATA.0
Rapid Mix Basin Drive Running | WTP_SEP_CLX | DI | Rapid Mix Basin Drive | Local:2:I.DATA.1
Rapid Mix Basin Drive Torque | WTP_SEP_CLX | DI | Rapid Mix Basin Drive | Local:2:I.DATA.2
Sedimentation Basin #1 Drive In-Auto | WTP_SEP_CLX | DI | Sedimentation Basin #1 Drive | Local:2:I.DATA.3 | x | x
Sedimentation Basin #1 Drive Running | WTP_SEP_CLX | DI | Sedimentation Basin #1 Drive | Local:2:I.DATA.4 | x | x | x
Sedimentation Basin #1 Drive Torque | WTP_SEP_CLX | DI | Sedimentation Basin #1 Drive | Local:2:I.DATA.5 | x | x | x
PV-1200 In-Auto | WTP_SEP_CLX | DI | PV-1200 | Local:2:I.DATA.6
Rapid Mix Basin #1 DriveStart/Stop | WTP_SEP_CLX | DO | Rapid Mix Basin Drive | Local:3:O.DATA.0
Sedimentation Basin #1 Drive Start/Stop | WTP_SEP_CLX | DO | Sedimentation Basin #1 Drive | Local:3:O.DATA.1
Sedimentation Basin Level Indication (LIT-1204) 0-15 Ft | WTP_SEP_CLX | AI | Sedimentation Basin Level Indication (LIT-1204) | Local:4:I.CH0DATA | x | x | IO Fault missing
To Rapid Mix Basin Flow (FIT-1200) 0-2 MGD | WTP_SEP_CLX | AI | To Rapid Mix Basin Flow (FIT-1200) | Local:4:I.CH1DATA
PV-1200 Position Indication 0-100% | WTP_SEP_CLX | AI | PV-1200 | Local:4:I.CH2DATA
PV-1200 Position Command 0-100% | WTP_SEP_CLX | AO | PV-1200 | Local:5:O.CH0DATA
Level Switch Low | WTP_HS_CLX | DI | HS WW Level Switch Low | Local:2:I.DATA.0 | x | x | x
Level Switch High | WTP_HS_CLX | DI | HS WW Level Switch High | Local:2:I.DATA.1 | x | x | x
Level Switch High High | WTP_HS_CLX | DI | HS WW Level Switch High High | Local:2:I.DATA.2 | x | x | x
Clear Well Level Indication (LIT-1300) 0-25 Ft | WTP_HS_CLX | AI | Clear Well Level Indication (LIT-1300) 0-25 Ft | Local:3:I.CH0DATA
To Distribution System Flow (FIT-1309) 0 - 2 MGD | WTP_HS_CLX | AI | To Distribution System Flow (FIT-1309) 0 - 2 MGD | Local:3:I.CH1DATA
Wetwell Level Indication (LIT-1302) 0 -25 Ft | WTP_HS_CLX | AI | HS WW Level Indication (LIT-1302) 0 -25 Ft | Local:3:I.CH2DATA | x | x | IO Fault missing | animation scaling not max at 15 ft
Wetwell Level Indication (LIT-1303) 0 -25 Ft | WTP_HS_CLX | AI | HS WW Level Indication (LIT-1303) 0 -25 Ft | Local:3:I.CH3DATA | x | x | IO Fault missing | animation scaling not max at 15 ft
Distribution System Level Indication (LIT-1305) 0- 20 Ft | WTP_HS_CLX | AI | Distribution System Level Indication (LIT-1305) 0- 20 Ft | Local:4:I.CH0DATA | x | x | IO Fault missing
HSP01_M1300_VSD | WTP_HS_CLX | VSD | HSP01_M1300_VSD |  | x | x | not tested
HSP02_M1301_VSD | WTP_HS_CLX | VSD | HSP02_M1301_VSD |  | x | x | not tested
FlocBsn01_M1202_VSD | WTP_SEP_CLX | VSD | FlocBsn01_M1202_VSD |  | x | x | did not test

## Equip
Equipment | EquipType | Start Permissives | Interlocks | Auto Control | Stats
LST1 Pump #1 | Pump | Inhibit Restart | LoWaterCutoff,HiMotorTemp,Fault | InchWorm Control | Runtime
LST1 Pump #2 | Pump | Inhibit Restart | LoWaterCutoff,HiMotorTemp,Fault | InchWorm Control | Runtime
LST1 LoLv | Float | NA | NA | NA | None
LST1 HiLv | Float | NA | NA | NA | None
LST1 Lv | Float | NA | NA | NA | None
WWTP Feed Pump #1 | Pump | Inhibit Restart | AlumTankLo,Fault,Overload | FlowPacing | Runtime
WWTP Feed Pump #2 | Pump | Inhibit Restart | AlumTankLo,Fault,Overload | FlowPacing | Runtime
WWTP Alum Tank Level | Level | NA | NA | NA | None
Areation Tank influent Flow | Flow | NA | NA | FlowPacing | Total
WWTP Bar Screen #1 | Screen | Inhibit Restart | None | RepeatCycleTimer | Runtime
WWTP Bar Screen #2 | Screen | Inhibit Restart | None | RepeatCycleTimer | Runtime
WWTP Grit Tank #1 Flow | Flow | NA | NA | None | Total
WWTP RW WW Level | Level | NA | NA | NA | None
WWTP RW WW Level Switch Low | Float | NA | NA | NA | None
WWTP RW WW Level Switch High | Float | NA | NA | NA | None
WWTP RW WW Level Switch High-High | Float | NA | NA | NA | None
WWTP Grit Tank #1 Drive | Drive | Inhibit Restart | None | RepeatCycleTimer | Runtime
WWTP Blower 400 (BLR-400) | Blower | Inhibit Restart | None | None | Runtime
WWTP Aeration Tank #1 Mixer #1 (M-400) | Mixer | Inhibit Restart | Fault | None | Runtime
WWTP Aeration Tank #1 Mixer #2 (M-401) | Mixer | Inhibit Restart | Fault | None | Runtime
WWTP Aeration Tank #2 Mixer #1 (M-402) | Mixer | Inhibit Restart | Fault | None | Runtime
WWTP Aeration Tank #2 Mixer #2 (M-403) | Mixer | Inhibit Restart | Fault | None | Runtime
WWTP Secondary Treatment Tank #1 Drive | Drive | Inhibit Restart | Torque | None | Runtime
WWTP Secondary Treatment Tank #2 Drive | Drive | Inhibit Restart | Torque | None | Runtime
WWTP Secondary Treatment Tank #1 RAS Pump (P-400) | Pump | Inhibit Restart | None | None | Runtime
WWTP Secondary Treatment Tank #2 RAS Pump (P-401) | Pump | Inhibit Restart | None | None | Runtime
WWTP Secondary Treatment Tank #1 RAS Pump Discharge Flow (FE-400) | Flow | NA | NA | None | Total
WWTP Secondary Treatment Tank #2 RAS Pump Discharge Flow (FE-401) | Flow | NA | NA | None | Total
WWTP Solids Storage Tank #1 Drive | Drive | Inhibit Restart | Torque | None | Runtime
WWTP Thickened WAS Tank Influent Position Valve (PV-600) | PositionValve | NA | NA | Flow Control | None
WWTP WAS Storage Tank Level Indication (LIT-605) 0-20 Ft | Level | NA | NA | NA | None
WWTP Solids Storage Tank Level Indication (LIT-603) 0-20 Ft | Level | NA | NA | NA | None
WWTP Secondary RAS To GBT Flow (FIT-600) 0-500 GPM | Flow | NA | NA | Flow Control | Total
WWTP Thickened WAS Tank To Solids Tank Pump (P-600) | Pump | Inhibit Restart | LoWaterCutoff,HiDischLevel,Fault | None | Runtime
WWTP Primary Treatment To Solids Tank Pump (P-601) | Pump | Inhibit Restart | HiDischLevel,Fault | None | Runtime
WWTP Solids Tank to Filter Press Pump (P-602) | Pump | Inhibit Restart | LoWaterCutoff,Fault | None | Runtime
WTP Bar Screen #1 | Screen | Inhibit Restart | None | RepeatCycleTimer | Runtime
WTP Bar Screen #2 | Screen | Inhibit Restart | None | RepeatCycleTimer | Runtime
WTP Grit Tank #1 Flow | Flow | NA | NA | None | Total
WTP RW WW Level | Level | NA | NA | NA | None
WTP RW WW Level Switch Low | Float | NA | NA | NA | None
WTP RW WW Level Switch High | Float | NA | NA | NA | None
WTP RW WW Level Switch High-High | Float | NA | NA | NA | None
WTP Grit Tank #1 Drive | Drive | Inhibit Restart | None | RepeatCycleTimer | Runtime
Rapid Mix Basin Drive | Drive | Inhibit Restart | Torque | None | Runtime
Sedimentation Basin #1 Drive | Drive | Inhibit Restart | Torque | None | Runtime
PV-1200 | PositionValve | None | None | None | None
Sedimentation Basin Level Indication (LIT-1204) | Level | None | None | None | None
To Rapid Mix Basin Flow (FIT-1200) | Flow | None | None | None | None
HS WW Level Switch Low | Float | None | None | None | None
HS WW Level Switch High | Float | None | None | None | None
HS WW Level Switch High High | Float | None | None | None | None
Clear Well Level Indication (LIT-1300) 0-25 Ft | Level | None | None | None | None
To Distribution System Flow (FIT-1309) 0 - 2 MGD | Flow | None | None | None | None
HS WW Level Indication (LIT-1302) 0 -25 Ft | Level | None | None | None | None
HS WW Level Indication (LIT-1303) 0 -25 Ft | Level | None | None | None | None
Distribution System Level Indication (LIT-1305) 0- 20 Ft | Level | None | None | None | None
HSP01_M1300_VSD | VSD | Inhibit Restart | LoWaterCutoff | PumpDemand | Runtime
HSP02_M1301_VSD | VSD | Inhibit Restart | LoWaterCutoff | PumpDemand | Runtime
FlocBsn01_M1202_VSD | VSD | Inhibit Restart | None | None | Runtime

## Tests
ROCKWELL TEST CASES
Control | Description | Test Scenario in simulate mode
Feed Pumps Flow Pacing | The pump will run and the output (feed rate) is controlled by the flow pacing signal and the dosage (adjustable at the HMI from 0- X ppm), The pump output in gallons per hour (feed rate) and stroke speed setpoint is calculated. The PLC will output the speed signal to the pump based on the appropriate flow pacing signal. | Adjust Flow, Length, dose levels to expected speed output levels
If pump 2 not available, pump 1 turns on
If pump 1 not available, pump 2 turns on
Flow Total | Daily & Yearly Totals | Test popup & values
AOI - Motor Demand | Raise level up & down see pump demand change, fault analog signal to see no pump demand | Set pumps to turn on at 1,2,3,4,5,6 Trip positions and Reset at .5,1.5,2.5,3.5,4.5,5.5. Increment level up and down to see that corresponding pumps turn on & Off
A faulted level signal turns all pumps off with demand = 0.
AOI - Motor Available | Inch worm logic, the logic starts/stops pump based on comparing the demand to the number of pumps running and then either start or stop the corresponding pump assigned to that position. Configurable up to 6 pumps. Position 1 Trip must be greater or Equal than Position 2 Trip. Position 1 Reset must be less or equal than Position 2 Reset. | If all pumps requested, the pumps come on at specified start order sequence 1 pump at a time.
If all pump demand = 0 while all pumps on, then the pumps turn off 1 pump at a time in reverse start order sequence at user configurable time source
If 4 pumps on, and 1 faults, then the next position (5) is called. If that position is not available then the next position (6) is called
Set P1 = Lag1, P2 = Lag3, P3 = Lag3, P4 = Lag4, P5 = Lag5, P6 = Lead Set wetwell level 3.5 ft. Only lead and Lag1 should start. (2 pumps)
AOI - Motor Rotation | See that each pump position rotates by 1 position, does not matter what order or how many pumps selected | Set pumps in motor 1 to position 1, motor 2 position 2 ect, then turn on at least one pump, all next values should be motor 1 pos 2, motor 2 pos 3 ect. The last position is rotated to first.
Transition to all pumps off, current values = next values.
ALL PUMPS OFF: Transition from operator to rotation, current = operate values, next = operate values rotated by one
ALL PUMPS OFF: Transition from rotation to operate, current = operate values, next = operate values
1=> PUMPS ON: Transition from operator to rotation, current does not change, next = Current values rotated by one
1=> PUMPS ON: Transition from rotation to operate, current does not change, next = operate values
RepeatCycleTimer | Repeat Cycle Timer will turn on for operator set time and off for operator set time and then repeat cycle. The cycle can be reset by the operator by pressing the "cycle now" button. The operater enters setpoint in minutes. There is logic for defining Hi & Lo setpoints. The logic gives On & Off time elapsed | Enter On time 1 min, Enter off Time 2 min, press cycle now button.
Enter in setpoint below & above the lo & hi limits
VSD | Variable Speed Drive, AOI block to power flex 700 VC 400 | HMI Operator entered 30 hz = drive indication of 30 hz
drive fault not tested
drive diagnostic indications not used
High Service Pumps | Pump Demand Logic | set trip first pump, first pump came on, set trip to second pump, second pump came on, set reset of second pump, second pump goes off, set reset of first pump, first pump goes off.
| Speed Band | set level at trip, speed = max, set level at mid trip& reset, speed = mid between min & max speed, set level at reset, speed = min